Annual Drinking Water Quality Report for 2025
Wilmington Water District

Town of Wilmington

PO Box 180 Wilmington, NY 12997

 (Public Water Supply ID NY1500300)
INTRODUCTION
To comply with State regulations, Wilmington Water District will be annually issuing a report describing the quality of your drinking water. The purpose of this report is to raise your understanding of drinking water and awareness of the need to protect our drinking water sources.  This report provides an overview of last year's water quality. Included are details about where your water comes from, what it contains, and how it compares to State standards.

If you have any questions about this report or concerning your drinking water, please contact Ed Orsi, Water Superintendent at (518) 946-7174 ext. 8. We want you to be informed about your drinking water. If you want to learn more, we would be pleased to discuss any drinking water issues in person or please feel free to attend any of our regularly scheduled town board meetings. The meetings are held the second Tuesday of each month at 6:00 PM at the Community Center on Springfield Road.

WHERE DOES OUR WATER COME FROM?
In general, the sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and, in some cases, radioactive material and can pick up substances resulting from the presence of animals or from human activities. Contaminants that may be present in source water include microbial contaminants, inorganic contaminants, pesticides and herbicides, organic chemical contaminants, and radioactive contaminants. In order to ensure that tap water is safe to drink, the State and the EPA prescribe regulations, which limit the concentration of certain contaminants in water provided by public water systems. The State Health Department's and the FDA's regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

Our water system serves approximately 1,042 people through 634 service connections. The water source consists of a dam impoundment on White Brook, which is located off the Whiteface Mountain Memorial Highway. A dam impoundment on Red Brook, located just north of White Brook, serves as an auxiliary water source. Water from both of these surface sources is filtered, disinfected, and treated for corrosion control prior to distribution.

ARE THERE CONTAMINANTS IN OUR DRINKING WATER?

As the State regulations require, we routinely test your drinking water for numerous contaminants. These contaminants include total coliform, turbidity, inorganic compounds, nitrate, nitrite, lead and copper, volatile organic compounds, total trihalomethanes, haloacetic acids, radiological and synthetic organic compounds. The table presented below depicts which compounds were detected in your drinking water. The State allows us to test for some contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of our data, though representative, is more than one year old.
It should be noted that all drinking water, including bottled drinking water, may be reasonably expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the EPA's Safe Drinking Water Hotline (1-800-426-4791) or the New York State Health Department (518) 891-1800.
	Table of Detected Contaminants

	Contaminant


	Violation

Yes/No


	Date of

Sample


	Level 

Detected

(Avg/Max)

(Range)
	Unit

Measure

-ment


	MCLG


	Regulatory Limit

(MCL, TT or AL)


	Likely Source of

Contamination



	Microbiological Contaminants

	Turbidity1
	no
	04/30/2025
	0.28
	NTU
	n/a
	TT=<1NTU
	Soil Runoff

	Turbidity1
	no
	2025
	100 % < 0.3
	NTU
	n/a
	TT=95% of samples <0.3NTU
	Soil Runoff

	Inorganic Contaminants

	 Nitrate
	no
	2025
	ND
	mg/L
	10
	10 (MCL)
	Runoff from fertilizer use; Leaky septic tanks, sewage; Erosion of natural deposits. 

	 Lead
	no
	2025
	0.02

(ND – 0.0056)3
	mg/L
	0.015
	0.015 (AL)
	Corrosion of household plumbing systems.

	Copper
	no
	2025
	0.252

(ND – 0.37)3
	mg/L
	1.3
	1.3 (AL)
	Corrosion of household plumbing systems.

	Fluoride
	no
	2025
	ND
	mg/L
	n/a
	2.2 (MCL)
	Naturally occurring.

	Zinc
	no
	2019
	0.034
	mg/L
	n/a
	5 (MCL)
	Naturally occurring; mining wastes

	Sodium
	no
	2023
	3.4
	mg/L
	n/a
	See Note 4
	Naturally occurring; Road salt; Water softeners; Animal waste.

	Chloride
	no
	2019
	5.1
	mg/L
	n/a
	250 (MCL)
	Naturally occurring or indicative of road salt contamination.

	Disinfection Byproducts – Stage 2

	Total Trihalomethanes (TTHMs)
	no
	2025

	32.55
9.6 – 44.56
	ug/L
	na
	80 (MCL)
	By-products of drinking water chlorination needed to kill harmful organisms.  TTHMs are formed when source water contains measurable amounts of organic matter.

	Haloacetic Acids
(HAAs)
	no
	2025
	36.95
11.8 – 59.46
	ug/l
	na
	60 (MCL)
	By-product of drinking water chlorination


Notes:

1 – Turbidity is a measure of the cloudiness of the water.  We test it because it is a good indicator of the effectiveness of our filtration system.  Our highest single turbidity measurement (0.28) for the year occurred on 04/30/2025.  State regulations require that turbidity must always be below 1 NTU.  The regulations require that 95% of the turbidity samples collected have measurements below 0.3 NTU.  We did not have any measurements that exceeded this criterion. All the measurements recorded were within the acceptable range allowed and did not constitute a treatment technique violation.
2 – The level presented represents the 90th percentile of the 10 sites tested.  A percentile is a value on a scale of 100 that indicates the percent of a distribution that is equal to or below it.  The 90th percentile is equal to or greater than 90% of the lead and copper values detected at your water system.  In this case, 10 samples were collected at your water system and the 90th percentile value was the 2nd highest value. 

3 – The level presented represents a range of the samples collected.  The action level for copper was not exceeded at any of the test sites. The action level for lead was exceeded at one sampling location. 

4 - Water containing more than 20 mg/l of sodium should not be used for drinking by people on severely restricted sodium diets. Water containing more than 270 mg/l of sodium should not be used for drinking by people on moderately restricted sodium diets.
5 – The value represents the highest Locational Running Annual Average of the samples collected.

6 – The values represent the range of the samples collected. 
Definitions:

Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible.

Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

Maximum Residual Disinfectant Level Goal (MRDLG): The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contamination.

Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

Treatment Technique (TT): A required process intended to reduce the level of a contaminant in drinking water.

Non-Detects (ND): Laboratory analysis indicates that the constituent is not present.

Nephelometric Turbidity Unit (NTU): A measure of the clarity of water. Turbidity in excess of 5 NTU is just noticeable to the average person.

Milligrams per liter (mg/l): Corresponds to one part of liquid in one million parts of liquid (parts per million - ppm).  
Micrograms per liter (ug/l): Corresponds to one part of liquid in one billion parts of liquid (parts per billion - ppb).

Picocuries per liter (pCi/L): A measure of the radioactivity in water.

WHAT DOES THIS INFORMATION MEAN?
As you can see by the table, our system had no violations.  We have learned through our testing that some contaminants have been detected; however, these contaminants were detected below the level allowed by the State.  Lead levels in our water system are relatively low; however, we did have one sampling site that exceeded the Action Level for lead.  We are required to provide the following information:  Lead can cause serious health effects in people of all ages, especially pregnant people, infants (both formula-fed and breastfed), and young children. Lead in drinking water is primarily from materials and parts used in service lines and in home plumbing.  The Wilmington Water District is responsible for providing high quality drinking water and removing lead pipes but cannot control the variety of materials used in the plumbing in your home. Because lead levels may vary over time, lead exposure is possible even when your tap sampling results do not detect lead at one point in time. You can help protect yourself and your family by identifying and removing lead materials within your home plumbing and taking steps to reduce your family's risk. Using a filter, certified by an American National Standards Institute accredited certifier to reduce lead, is effective in reducing lead exposures. Follow the instructions provided with the filter to ensure the filter is used properly. Use only cold water for drinking, cooking, and making baby formula. Boiling water does not remove lead from water. Before using tap water for drinking, cooking, or making baby formula, flush your pipes for several minutes. You can do this by running your tap, taking a shower, doing laundry or a load of dishes. If you have a lead service line or galvanized requiring replacement service line, you may need to flush your pipes for a longer period. If you are concerned about lead in your water and wish to have your water tested, contact the Wilmington Water Superintendent – Ed Orsi at (518) 946-7210.   Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available at https://www.epa.gov/safewater/lead.
IS OUR WATER SYSTEM MEETING OTHER RULES THAT GOVERN OPERATIONS?
Last year our system was in compliance with applicable State drinking water operating, monitoring and reporting requirements, including the preparation of a lead service line inventory. This inventory is publicly available and can be accessed at the Wilmington Town Office.  
INFORMATION ON LEAD SERVICE LINE INVENTORY
The Town of Wilmington completed a Lead Service Line Inventory (LSLI) of the Wilmington Water District and submitted it to the NYS Department of Health on November 14, 2025.  Our system has a total of 634 service connections.  We have identified all 634 of these service lines.  There are no lead service lines in our system, but we do have 4 galvanized service line that are required to be replaced.  Thank you for your help in completing this inventory.
SOURCE WATER ASSESSMENT SUMMARY
The NYS Department of Health completed a source water assessment for this system based on available information.  The assessment area for this drinking water source contains no discrete PCSs, and none of the land cover contaminant prevalence ratings are greater than low. However, the high mobility of microbial contaminants in reservoirs results in this drinking water intake having medium-high susceptibility ratings for protozoa and enteric bacteria and viruses. Furthermore, reservoirs are highly susceptible to water quality problems caused by phosphorus additions. The health department will use this information to direct future source water protection activities.  These may include water quality monitoring, resource management, planning, and education programs. A copy of the assessment, including a map of the assessment area, can be obtained by contacting us as noted below.
DO I NEED TO TAKE SPECIAL PRECAUTIONS?

Although our drinking water met or exceeded state and federal regulations, some people may be more vulnerable to disease causing microorganisms or pathogens in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice from their health care provider about their drinking water. EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium, Giardia and other microbial pathogens are available from the Safe Drinking Water Hotline (800-426-4791).

WHY SAVE WATER AND HOW TO AVOID WASTING IT?
Although our system has an adequate amount of water to meet present and future demands, there are a number of reasons why it is important to conserve water:
· Saving water saves energy and some of the costs associated with both of these necessities of life;

· Saving water reduces the cost of energy required to pump water and the need to construct costly new wells, pumping systems and water towers; and

· Saving water lessens the strain on the water system during a dry spell or drought, helping to avoid severe water use restrictions so that essential fire fighting needs are met. You can play a role in conserving water by becoming conscious of the amount of water your household is using, and by looking for ways to use less whenever you can. 
It is not hard to conserve water. Conservation tips include:
· Automatic dishwashers use 15 gallons for every cycle, regardless of how many dishes are loaded. So get a run for your money and load it to capacity. Turn off the tap when brushing your teeth.

· Check every faucet in your home for leaks. Just a slow drip can waste 15 to 20 gallons a day. Fix it and you can save almost 6,000 gallons per year.

· Check your toilets for leaks by putting a few drops of food coloring in the tank, watch for a few minutes to see if the color shows up in the bowl. It is not uncommon to lose up to 100 gallons a day from one of these otherwise invisible toilet leaks. Fix it and you save more than 30,000 gallons a year.

CLOSING
Thank you for allowing us to continue to provide your family with quality drinking water this year. In order to maintain a safe and dependable water supply we sometimes need to make improvements that will benefit all of our customers. The costs of these improvements may be reflected in the rate structure. Rate adjustments may be necessary in order to address these improvements. We ask that all our customers help us protect our water sources, which are the heart of our community. Please call our office at (518) 946-7174 ext. 8 if you have questions.

